SPECIFICATIONS FOR THE EXPENSE BOOK

For installations with a consumption of > 2800 l/h

(industry, schools, buildings with multiple consumption…)

YDROSTOP – WATER SAFETY DEVICE

Description

The water safety devices are mounted directly behind the split on the reduced sections.

These devices almost immediately shut off the water supply in case of a break in the water pipe.

In addition, they prevent unnecessary water consumption.

Depending on a preset time (from 15 minutes up to 2 hours), the water supply will be cut off in case of a leak in the water pipe or uninterrupted water consumption.

The device's operation is based on a difference in pressure .

If the device registers a big difference in pressure (fracture) the water supply is cut off almost at once.

At normal water consumption (smaller pressure difference), the time mechanism will be activated which cuts off the water supply after the pre-set time.

After turning the leaking tap off, the devices will reset/reopen after a few seconds (if the devices are in automatic mode).

After a small amount of water has been tapped off, the time mechanism will be reset, and a new complete preset time will be available.

The devices are made of a synthetic material manufactured under high pressure.

All materials used comply with the national and international standards for drinking-water quality.

The device is equipped with:

- a separate pre-filter equipped with coupling pieces ¾ “ connection

- a non-return valve

- an adjustable time mechanism from 15 to 120 minutes

- automatic reset; after a few seconds, after shut-off of the water consumer

Technical specifications

Normal working pressure  	0.5 – 6 bar

Pressure tested to 	     	22 bar

Flow 			     	25 to 2800 l/h (option 1700 l/h)

Pressure loss		     	0.2 – 0.7 bar

Weight Ydrostop+Filter      	1.2 kg

Temperature 		   	+ 1ºC - +30ºC

Connection Ydrostop 	    	1 ½“ BSP

Connection Filter	    	1’’  &  ¾” BSP

Dimensions Ydrostop+Filter   	L x H x W   350 x 250 x 75 mm.

Execution

Installation Ydrostop + Filter horizontal, incl. 2 stop valves and bypass with stop valve with the same diameter as the existing pipe.

Install Ydrostop in accordance with the prescriptions of the manufacturer.

A  Closed for e.g.: filling of pools, long-lasting consumption...

B  Stopcock for very fast reset (manual reset)

C. Open for e.g.: filling of pools, long-lasting consumption...

(1) For smaller or greater flow (2800 l/h), please contact the manufacturer.